## sheet1
| tag_EN | type | alpha1 | alpha2 | beta2 | beta1 | 齿轮箱 | 发电机 | 变桨 | 变频器 | 偏航 | 液压 | 转速 | 振动
rece_time | rece_time
realdata | realdata
wtid | wtid | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
real_time | real_time | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
机组运行模式 | giWindTurbineOperationMode | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
电网有功功率 | grGridActivePower
发电机转速1 | grGeneratorSpeed1 | 2 | 0 | 374 | 378 | 400 | 1 | 1 | 1 |  |  |  | 1 | 1
风速 | grWindSpeed | 2 | 1.59 | 3 | 20 | 25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
风向对北角度 | grWindDirctionToNorth | 2 | 0 | 95 | 160 | 350 |  |  |  |  | 1 | 1
桨叶角度1A | grPitchAngle1A | 1 | -0.5 | 0 | 5 | 30 |  |  | 1 |  |  |  | 1 | 1
桨叶角度1B | grPitchAnge1B | 1 | -0.5 | 0 | 5 | 30
桨叶角度2A | grPitchAngle2A | 1 | -0.5 | 0 | 5 | 30 |  |  | 1 |  |  |  | 1 | 1
桨叶角度2B | grPitchAnge2B | 1 | -0.5 | 0 | 5 | 30
桨叶角度3A | grPitchAngle3A | 1 | -0.5 | 0 | 5 | 30 |  |  | 1 |  |  |  | 1 | 1
桨叶角度3B | grPitchAnge3B | 1 | -0.5 | 0 | 5 | 30
机舱振动Y1 | grNacelleVibrationY1 | 2 | -0.1 | -0.07 | 0.076 | 0.1 | 1 | 1 | 1 |  | 1 | 1 | 1
机舱振动Y2 | grNacelleVibrationY2 | 2 | -0.1 | -0.076 | 0.069 | 0.1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1
机舱振动X1 | grNacelleVibrationX1 | 2 | -0.1 | -0.08 | 0.083 | 0.1 | 1 | 1 | 1 |  | 1 | 1 | 1
机舱振动X2 | grNacelleVibrationX2 | 2 | -0.1 | -0.076 | 0.07 | 0.1 | 1 | 1 | 1 |  | 1 | 1 | 1
塔基控制柜温度 | grTowerBaseCabinetTemperture
塔基温度 | grTowerBaseTemperature
机舱控制柜温度 | grNacelleCabinetTemperture
机舱温度 | grNacelleTemperture | 2 | 3.1 | 15.3 | 39.7 | 52 | 1 | 1 |  |  | 1 | 1
机舱对北角度 | grNacellePositionToNorth | 2 | 0 | 95 | 160 | 350 |  |  |  |  | 1 | 1 | 1
电机1温度 | grPitchMotorTemperture1 | 2 | -7.3 | 27 | 77 | 130 |  |  | 1
电机2温度 | grPitchMotorTemperture2 | 2 | -8.7 | 26 | 85 | 130 |  |  | 1
电机3温度 | grPitchMotorTemperture3 | 2 | -3.3 | 30 | 86 | 130 |  |  | 1
grPitchBackupPowerCabinetTemperture1 | grPitchBackupPowerCabinetTemperature1
grPitchBackupPowerCabinetTemperture2 | grPitchBackupPowerCabinetTemperature2
grPitchBackupPowerCabinetTemperture3 | grPitchBackupPowerCabinetTemperature3
轮毂温度 | grHubTemperture | 2 | 4.8 | 17 | 42 | 55 |  |  | 1
齿轮箱前轴承温度 | grGearboxHubSideBearingTemperature | 2 | 46 | 47 | 63.9 | 70 | 1 | [5 empty] | 1
齿轮箱后轴承温度 | grGearboxGeneratorSideBearingTemperature | 2 | 41.8 | 46.4 | 65.4 | 70 | 1 | [5 empty] | 1
齿轮箱主轴承温度 | grGearboxMainBearingTemperature | 2 | 9.7 | 26 | 49.5 | 70 | 1 | [5 empty] | 1
齿轮箱油温 | grGearBoxOilTemperture | 2 | 20 | 40 | 58.1 | 65 | 1 | 1 |  |  |  |  | 1
发电机前轴承温度 | grGeneratorGearboxSideBearingTemperature | 2 | 33 | 47.3 | 68.2 | 85 |  | 1 |  |  |  |  | 1
发电机后轴承温度 | grGeneratorNacelleSideBearingTemperature | 2 | 20.6 | 47.5 | 82.1 | 85 |  | 1 |  |  |  |  | 1
发电机绕组温度1 | grGeneratorWindingTemperature1 | 2 | 75 | 86.1 | 108.5 | 120 |  | 1
发电机绕组温度2 | grGeneratorWindingTemperature2 | 2 | 75 | 86.1 | 108.5 | 120 |  | 1
发电机绕组温度3 | grGeneratorWindingTemperature3 | 2 | 75 | 86.1 | 108.5 | 120 |  | 1
发电机绕组温度4 | grGeneratorWindingTemperature4 | 2 | 75 | 86.1 | 108.5 | 120 |  | 1
发电机绕组温度5 | grGeneratorWindingTemperature5 | 2 | 75 | 86.1 | 108.5 | 120 |  | 1
发电机绕组温度6 | grGeneratorWindingTemperature6
室外温度 | grOutdoorTemperature
塔基变压器温度 | grTransformerTemperture
机组当天发电量 | grWindTurbineEnergyOutputDay
机组总发电量 | grWindTurbineEnergyOutputAll
机组当天可利用率 | WindTurbineAvailableRateDay
电网电压L1 | grGridVoltageL1 | 2 | 650 | 670 | 690 | 710 |  |  |  | 1
电网电压L2 | grGridVoltageL2
电网电压L3 | grGridVoltageL3
电网频率 | grGridFrequence | 2 | 49.545 | 49.88 | 50.15 | 50.285 |  |  |  | 1
电网电流L1 | grGridCurrentL1
电网电流L2 | grGridCurrentL2
电网电流L3 | grGridCurrentL3
机组故障模式 | giWindTurbineErrorMode
功率设定值 | grPowerSetPoint
叶轮转速1 | grRotorSpeed1 | 2 | 0.04 | 4.13 | 12.51 | 16.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
叶轮转速2 | grRotorSpeed2 | 2 | 0.73 | 4.8 | 12.7325 | 16.8
grTempWaterGearCooling_1sec | grTempWaterGearCooling_1sec
TurbineStatus | TurbineStatus
entercount | entercount
EnterType | EnterType
reserved1 | reserved1
reserved2 | reserved2
reserved3 | reserved3
reserved4 | reserved4
reserved5 | reserved5
reserved6 | reserved6
reserved7 | reserved7
reserved8 | reserved8
reserved9 | reserved9
reserved10 | reserved10
机组偏航模式 | giWindTurbineYawMode
机组总运行时间 | grWindTurbineRunTimeAll
grWindTurbineRunTimeDay | grWindTurbineRunTimeDay
机组当天运行时间 | WindTurbineAvailableTimeDay
机组当天故障时间 | grWindTurbineErrorTimeDay
机组总用电量 | grWindTurbineEneryConsumeDay
机组总可利用率 | WindTurbineAvailableRateAll
桨叶角度1B | grPitchAngle1B
桨叶角度2B | grPitchAngle2B
桨叶角度3B | grPitchAngle3B
变桨角度设定值1 | grPitchAngleSetPoint1 | 1 | -0.5 | 0 | 5 | 30
变桨角度设定值2 | grPitchAngleSetPoint2 | 1 | -0.5 | 0 | 5 | 30
变桨角度设定值3 | grPitchAngleSetPoint3 | 1 | -0.5 | 0 | 5 | 30
桨叶1变桨速度 | grPitchSpeed1 |  |  |  | 5
桨叶2变桨速度 | grPitchSpeed2 |  |  |  | 5
桨叶3变桨速度 | grPitchSpeed3 |  |  |  | 5
桨叶1电机电流 | grPitchMotorCurrent1 | 2 | -111 | 0.4 | 85.2 | 111 |  |  | 1
桨叶2电机电流 | grPitchMotorCurrent2 | 2 | -111 | 0.4 | 76.8 | 111 |  |  | 1
桨叶3电机电流 | grPitchMotorCurrent3 | 2 | -111 | 0.4 | 110.3 | 111 |  |  | 1
电池箱1温度 | grPitchBackupPowerCabinetTemperture1 | 2 | 3.8 | 16 | 45 | 62 |  |  | 1
电池箱2温度 | grPitchBackupPowerCabinetTemperture2 | 2 | 17.8 | 18 | 40 | 62 |  |  | 1
电池箱3温度 | grPitchBackupPowerCabinetTemperture3 | 2 | 17.8 | 18 | 40 | 62 |  |  | 1
轴1箱温度 | grPitchDriverCabinetTemperture1 | 2 | -10 | 22 | 54 | 62 |  |  | 1
轴2箱温度 | grPitchDriverCabinetTemperture2 | 2 | -10 | 23 | 50 | 62 |  |  | 1
轴3箱温度 | grPitchDriverCabinetTemperture3 | 2 | -10 | 27 | 52 | 62 |  |  | 1
齿轮箱油位 | grGearboxOilLevel | 2 | 30 | 31.43 | 72.35 | 80 | 1
A1口压力 | grGearboxOilPressureA1 | 2 | 0.02 | 0.279 | 0.618 | 2 | 1
A2口压力 | grGearboxOilPressureA2 | 2 | 0.5 | 1.925 | 4.575 | 6 | 1
A3口压力 | grGearboxOilPressureA3 | 2 | 0.5 | 1.035 | 2.239 | 4 | 1
A4口压力 | grGearboxOilpressureA4 | 2 | 0.7 | 3.825 | 5.668 | 13 | 1 | 1
储能罐压力 | grGearboxEnergyTankPressure
液压系统压力 | grHydraulicSystemPressure | 2 | 120 | 140 | 160 | 175 |  |  |  |  | 1 | 1 |  | 1
偏航压力 | grHydraulicYawBrakePressure | 2 | 20 | 140 | 160 | 175 |  |  |  |  | 1 | 1 |  | 1
主轴刹车压力 | grHydraulicRotorBrakePressure | 2 | -1 | -0.51 | 1 | 3 | [5 empty] | 1 | 1 | 1
发电机水泵进水压力 | grGeneratorWaterPressureIn | 2 | 1 | 2 | 3 | 5 |  | 1
发电机水泵出水压力 | grGeneratorWaterPressureOut | 2 | 1 | 2.75 | 6.25 | 8 |  | 1
发电机水泵进水温度 | grGeneratorWaterTemperatureIn | 2 | 22.8 | 29 | 45 | 55 |  | 1
发电机水泵出水温度 | grGeneratorWaterTemperatureOut | 2 | 15.6 | 26 | 45.6 | 55 |  | 1
扭缆角度 | grYawTwistPosition
风向 | grWindDirction | 2 | -152.015 | -74.68 | 79.79 | 157.125 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
大气压力 | grAirPressure
空气密度 | grAirDensity
发电机转速2 | grGeneratorSpeed2
变频器发电机转速 | grConverterGeneratorSpeed | 2 | 0 | 374 | 378 | 400 |  | 1 |  | 1 |  |  | 1
电网无功功率 | grGridReactivePower
变频器机侧电压 | GeneratorSideVoltage
变频器直流母排电压 | grConverterGridVoltage | 2 | 650 | 670 | 690 | 710 |  |  |  | 1 |  |  | 1
功率模块温度 | grConverterPowerModuleTemperture | 2 | 11.345 | 22.75 | 45.16 | 56.365 |  |  |  | 1
CoolingWaterTemperture | CoolingWaterTemperture
变频器CP剩余能力 | grConverterCP
降功率转速设定值 | PowerReductionTorqueSetpoint
变频器合闸 | gbConverterReadyOn
变频器运行 | gbConverterReadyRun
低穿信号 | gbLVRTActived
齿轮箱油泵1高速 | gbGearboxPumpHighSpeedOn1
齿轮箱油泵2高速 | gbGearboxPumpHighSpeedOn2
齿轮箱油泵1低速 | gbGearboxPumpLowerSpeedOn1
齿轮箱油泵2低速 | gbGearboxPumpLowerSpeedOn2
齿轮箱加热器 | gbGearboxBypasspumpOn
齿轮箱旁通泵 | gbGearboxOilHeaterOn
齿轮箱油冷风扇 | gbGearboxOilFanOn
液压泵 | gbHydraulicPumpOn
叶轮锁定销1锁定 | gbRotorLock1Actived
叶轮锁定销2锁定 | gbRotorLock2Actived
叶轮锁定销1释放 | gbRotorLock1Deactived
叶轮锁定销2释放 | gbRotorLock2Deactived
发电机水泵 | gbGeneratorWaterPumpOn
发电机水冷风扇 | gbGeneratorWaterFanOn
发电机水加热器 | gbGeneratorWaterHeaterOn
偏航CW | gbYawCW
偏航CCW | gbYawCCW
故障编码1 | giErrorCode1
故障编码2 | giErrorCode2
故障编码3 | giErrorCode3
故障编码4 | giErrorCode4
故障编码5 | giErrorCode5
故障编码6 | giErrorCode6
故障编码7 | giErrorCode7
故障编码8 | giErrorCode8
故障编码9 | giErrorCode9
故障编码10 | giErrorCode10
故障编码11 | giErrorCode11
故障编码12 | giErrorCode12
故障编码13 | giErrorCode13
故障编码14 | giErrorCode14
故障编码15 | giErrorCode15
故障编码16 | giErrorCode16
故障编码17 | giErrorCode17
故障编码18 | giErrorCode18
故障编码19 | giErrorCode19
故障编码20 | giErrorCode20
故障编码21 | giErrorCode21
故障编码22 | giErrorCode22
故障编码23 | giErrorCode23
故障编码24 | giErrorCode24
故障编码25 | giErrorCode25
故障编码26 | giErrorCode26
故障编码27 | giErrorCode27
故障编码28 | giErrorCode28
故障编码29 | giErrorCode29
故障编码30 | giErrorCode30
grWindTurbineStandByTime | grWindTurbineStandByTime
grEneryConsumeDaily | grEneryConsumeDaily
grWindTurbineOerationTime | grWindTurbineOerationTime
grPowerProductionTime | grPowerProductionTime
grWindTurbineErrorTime | grWindTurbineErrorTime
grWindTurbineServiceTime | grWindTurbineServiceTime
grWindOKtime | grWindOKtime
grGridErrorTime | grGridErrorTime
gdiEneryOutput | gdiEneryOutput
grAvailableTime | grAvailableTime
grEneryConsume | grEneryConsume
grWindTurbineStandByTimeDaily | grWindTurbineStandByTimeDaily
grWindTurbineOerationTimeDaily | grWindTurbineOerationTimeDaily
grPowerProductionTimeDaily | grPowerProductionTimeDaily
grWindTurbineErrorTimeDaily | grWindTurbineErrorTimeDaily
grWindTurbineServiceTimeDaily | grWindTurbineServiceTimeDaily
grWindOKtimeDaily | grWindOKtimeDaily
grGridErrorTimeDaily | grGridErrorTimeDaily
grAvailableTimeDaily | grAvailableTimeDaily
grEneryOutputDaily | grEneryOutputDaily
giFirstErrorNumber | giFirstErrorNumber
grGearboxMainPumpOnTime1 | grGearboxMainPumpOnTime1
grGearboxMainPumpOnTime2 | grGearboxMainPumpOnTime2
grGearboxBypasspumpOnTime | grGearboxBypasspumpOnTime
grGearboxOilHeaterOnTime | grGearboxOilHeaterOnTime
grGearboxOilFanOnTime | grGearboxOilFanOnTime
grGeneratorWaterPumpOnTime | grGeneratorWaterPumpOnTime
grGeneratorWaterFanOnTime | grGeneratorWaterFanOnTime
grGeneratorWaterHeaterOnTime | grGeneratorWaterHeaterOnTime
grHydraulicPumpOnTime | grHydraulicPumpOnTime
grYawTime | grYawTime
grNacelleFanOnTime | grNacelleFanOnTime
giGearboxMainPumpOnTimes1 | giGearboxMainPumpOnTimes1
giGearboxMainPumpOnTimes2 | giGearboxMainPumpOnTimes2
giGearboxBypassPunpOnTimes | giGearboxBypassPunpOnTimes
giGearboxOilHeaterOnTimes | giGearboxOilHeaterOnTimes
giGearboxOilFanOnTimes | giGearboxOilFanOnTimes
giGearboxOilCoolerBypassValveTimes | giGearboxOilCoolerBypassValveTimes
giGearboxOilVolumeValveTimes | giGearboxOilVolumeValveTimes
giGeneratorWaterPumpOnTimes | giGeneratorWaterPumpOnTimes
giGeneratorWaterFanOnTimes | giGeneratorWaterFanOnTimes
giGeneratorWaterHeaterOnTimes | giGeneratorWaterHeaterOnTimes
giHydraulicPumpOnTimes | giHydraulicPumpOnTimes
giYawTimes | giYawTimes
giNacelleFanOnTimes | giNacelleFanOnTimes
变频器扭矩 | grConverterTorque | 3 | 0 | 25 | 75 | 100 |  |  |  | 1 |  |  | 1 | 1
扭矩设定值 | grTorqueSetpoint | 3 | 0 | 25 | 75 | 100 |  |  | 1 | 1 |  |  | 1
扭矩设定比较值 | grConverterTorque/grTorqueSetpoint | 2 | 0.9 | 0.92 | 1.08 | 1.1 |  |  |  | 1 |  |  | 1
grPowerDemand | grPowerDemand |  | 0 | 15.5 | 2299 | 3000
变频器功率 | grCoverterPower | 3 | 0 | 15.5 | 2299 | 3000 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
grPitchPositionSetpoint | grPitchPositionSetpoint |  | -6.2 | 122 | 378 | 506
发电机转速设定值 | grGeneratorSpeedSetpoint | 3 | 0 | 122 | 378 | 378 |  | 1 |  |  |  |  | 1 | 1
无功功率设定值 | grReactPowerSetPoint
功率因数设定值 | grCosSetPoint
电压设定值 | grVoltageSetPoint
设定时间年 | giPLCTimeSettingYear
设定时间月 | giPLCTimeSettingMonth
设定时间日 | giPLCTimeSettingDay
设定时间小时 | giPLCTimeSettingHour
设定时间分钟 | giPLCTimeSettingMin
设定时间秒 | giPLCTimeSettings
设定时间毫秒 | giPLCTimeSettingms
设定时间周 | giPLCTimeSettingWeek
机组维护 | gbWindturbineService
远程手动偏航 | gbRemoteYawEnable
CW偏航 | gbRemoteYawCW
CCW偏航 | gbRemoteYawCCW
停机 | gbRemoteStopWindTuebine
启动 | gbRemoteStartWindTuebine
复位 | gbRemoteResetWindTuebine
功率因数设定 | gbCosSetActive
无功功率设定 | gbReactPowerSetActive
电压设定 | gbVoltageSetActive
系统时间设定 | gbPLCTimeSetActive
机组当天可运行时间 | grWindTurbineAvailableTimeDay
grWindTurbineAvailableRateAll | grWindTurbineAvailableRateAll
grWindTurbineAvailableRateDay | grWindTurbineAvailableRateDay
grGearboxMainBearingTempertureemperature | grGearboxMainBearingTempertureemperature
grGearboxHubSideBearingTempertureemperature | grGearboxHubSideBearingTempertureemperature
grGearboxGeneratorSideBearingTempertureemperature | grGearboxGeneratorSideBearingTempertureemperature
grGeneratorWindingTemperature1 | grGeneratorWindingTemperature1
grGeneratorWindingTemperature2 | grGeneratorWindingTemperature2
grGeneratorWindingTemperature3 | grGeneratorWindingTemperature3
grGeneratorWindingTemperature4 | grGeneratorWindingTemperature4
grGeneratorWindingTemperature5 | grGeneratorWindingTemperature5
grGeneratorWindingTemperature6 | grGeneratorWindingTemperature6
grGeneratorGearboxSideBearingTempertureemperature | grGeneratorGearboxSideBearingTempertureemperature
grGeneratorNacelleSideBearingTempertureemperature | grGeneratorNacelleSideBearingTempertureemperature
grHydraulicRotorBrakePressure | grHydraulicRotorBrakePressure
grGeneratorWaterTemperatureIn | grGeneratorWaterTemperatureIn
grGeneratorWaterTemperatureOut | grGeneratorWaterTemperatureOut
grConverterGeneratorSideVoltage | grConverterGeneratorSideVoltage
grConverterPowerModuleTemperture | grConverterPowerModuleTemperture
变频器冷却水温度 | grConverterCoolingWaterTemperture
grConverterPowerReductionTorqueSetpoint | grConverterPowerReductionTorqueSetpoint
gbTurbineInSpecting | gbTurbineInSpecting
gbTurbinePowerLimited | gbTurbinePowerLimited
grGearboxOilTemperatureAtMainPump | grGearboxOilTemperatureAtMainPump
grGearboxOilTemperatureAtBypassPump | grGearboxOilTemperatureAtBypassPump
grGearboxOilTemperatureAtReturnOil | grGearboxOilTemperatureAtReturnOil
grHydraulicRotorLockPressure | grHydraulicRotorLockPressure
giFirstErrorNumber1 | giFirstErrorNumber1
giFirstErrorNumber2 | giFirstErrorNumber2
giFirstErrorNumber3 | giFirstErrorNumber3
giFirstErrorNumber4 | giFirstErrorNumber4
giFirstErrorNumber5 | giFirstErrorNumber5
giFirstErrorNumber6 | giFirstErrorNumber6
giFirstErrorNumber7 | giFirstErrorNumber7
giFirstErrorNumber8 | giFirstErrorNumber8
giFirstErrorNumber9 | giFirstErrorNumber9
giFirstErrorNumber10 | giFirstErrorNumber10
giFirstErrorNumber11 | giFirstErrorNumber11
giFirstErrorNumber12 | giFirstErrorNumber12
giFirstErrorNumber13 | giFirstErrorNumber13
giFirstErrorNumber14 | giFirstErrorNumber14
giFirstErrorNumber15 | giFirstErrorNumber15
giFirstErrorNumber16 | giFirstErrorNumber16
giFirstErrorNumber17 | giFirstErrorNumber17
giFirstErrorNumber18 | giFirstErrorNumber18
giFirstErrorNumber19 | giFirstErrorNumber19
giFirstErrorNumber20 | giFirstErrorNumber20
giFirstErrorNumber21 | giFirstErrorNumber21
giFirstErrorNumber22 | giFirstErrorNumber22
giFirstErrorNumber23 | giFirstErrorNumber23
giFirstErrorNumber24 | giFirstErrorNumber24
giFirstErrorNumber25 | giFirstErrorNumber25
giFirstErrorNumber26 | giFirstErrorNumber26
giFirstErrorNumber27 | giFirstErrorNumber27
giFirstErrorNumber28 | giFirstErrorNumber28
giFirstErrorNumber29 | giFirstErrorNumber29
giFirstErrorNumber30 | giFirstErrorNumber30
gdtFirstErrorTrigTime1 | gdtFirstErrorTrigTime1
gdtFirstErrorTrigTime2 | gdtFirstErrorTrigTime2
gdtFirstErrorTrigTime3 | gdtFirstErrorTrigTime3
gdtFirstErrorTrigTime4 | gdtFirstErrorTrigTime4
gdtFirstErrorTrigTime5 | gdtFirstErrorTrigTime5
gdtFirstErrorTrigTime6 | gdtFirstErrorTrigTime6
gdtFirstErrorTrigTime7 | gdtFirstErrorTrigTime7
gdtFirstErrorTrigTime8 | gdtFirstErrorTrigTime8
gdtFirstErrorTrigTime9 | gdtFirstErrorTrigTime9
gdtFirstErrorTrigTime10 | gdtFirstErrorTrigTime10
gdtFirstErrorTrigTime11 | gdtFirstErrorTrigTime11
gdtFirstErrorTrigTime12 | gdtFirstErrorTrigTime12
gdtFirstErrorTrigTime13 | gdtFirstErrorTrigTime13
gdtFirstErrorTrigTime14 | gdtFirstErrorTrigTime14
gdtFirstErrorTrigTime15 | gdtFirstErrorTrigTime15
gdtFirstErrorTrigTime16 | gdtFirstErrorTrigTime16
gdtFirstErrorTrigTime17 | gdtFirstErrorTrigTime17
gdtFirstErrorTrigTime18 | gdtFirstErrorTrigTime18
gdtFirstErrorTrigTime19 | gdtFirstErrorTrigTime19
gdtFirstErrorTrigTime20 | gdtFirstErrorTrigTime20
gdtFirstErrorTrigTime21 | gdtFirstErrorTrigTime21
gdtFirstErrorTrigTime22 | gdtFirstErrorTrigTime22
gdtFirstErrorTrigTime23 | gdtFirstErrorTrigTime23
gdtFirstErrorTrigTime24 | gdtFirstErrorTrigTime24
gdtFirstErrorTrigTime25 | gdtFirstErrorTrigTime25
gdtFirstErrorTrigTime26 | gdtFirstErrorTrigTime26
gdtFirstErrorTrigTime27 | gdtFirstErrorTrigTime27
gdtFirstErrorTrigTime28 | gdtFirstErrorTrigTime28
gdtFirstErrorTrigTime29 | gdtFirstErrorTrigTime29
gdtFirstErrorTrigTime30 | gdtFirstErrorTrigTime30
grPowerChangeRate | grPowerChangeRate
grMinPowerSetpoint | grMinPowerSetpoint
grActivePowerSetpointFeedback | grActivePowerSetpointFeedback
giRemoteStopTurbineFeedback | giRemoteStopTurbineFeedback
gwRemotePowerLimitEnable | gwRemotePowerLimitEnable
gbStopTurbine | gbStopTurbine
gbStartTurbine | gbStartTurbine
grReactivePowerSetpoint | grReactivePowerSetpoint
grActivePowerSetpoint | grActivePowerSetpoint
giPowerReductionType | giPowerReductionType
grCorrectedWindSpeed | grCorrectedWindSpeed
TurbineTableName | TurbineTableName
WindSpeed | WindSpeed
Power | Power
GenEnergy | GenEnergy
RunCode | RunCode
WindSpeedStatus | WindSpeedStatus
LimitPowerStatus | LimitPowerStatus
PowerCon | PowerCon
桨叶角度1A与变桨角度设定值1差值 | grPitchAngle1A-grPitchAngleSetPoint1 |  | 2.07 |  |  | 1.76 |  |  | 1
桨叶角度2A与变桨角度设定值2差值 | grPitchAngle2A-grPitchAngleSetPoint2 |  | -2.04 |  |  | 1.8
桨叶角度3A与变桨角度设定值3差值 | grPitchAngle3A-grPitchAngleSetPoint3 |  | -2.06 |  |  | 1.77